## INCREASE, LABOR, 911, WARRANTY,
FOLLOWING ARE CONTRACTUAL |  |  |  |  | 1.12
OVERALL INCREASE % | PLUMBING LABOR RATE |  | EMERGENCY CALL OUT
INCREASE % | PREVIOUS | NEW LABOR/HR | PREVIOUS | NEW LABOR/HR
1.05 | 165 | 175 | 250 | 270
1 |  This is an over ride
2 YEAR WARRANTY 1/17/18 | 3 YEAR WARRANTY 1/17/18 | 4 YEAR WARRANTY 1/17/18 | 5 YEAR WARRANTY 1/17/18 | 6 YEAR WARRANTY 1/17/18
300 | 200 | 100 | 50 | 0
 This is an over ride
TAX RATE %
1.07
MARK UP %
1.3
END
PERMIT PRICING
HYDRONIC BOILER |  | 485
STEAM BOILER |  | 485
COMBO UNIT |  | 485
FURNACE |  | 485
CHIMNEY LINER |  | 125
NORMAL DHW |  | 415
PV DHW |  | 415
TANKLESS DHW |  | 485
END

## A-C Complete
COIL – CONDENSER – LINE SET
Quantity | Description | UNIT PRICE | LINE TOTAL
GOODMAN A/C SYSTEMS
| A/C COIL-CONDENSER-LINE SET |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | GOODMAN 16 SEER, 2-ton R410A, GSX16024, ¾ Line Set | 3591.5393 | 3591.5393 | Coil | 358.91 | 1.05 | 376.8555 | 1.07 | 403.2354 | 1.3 | 524.206 | 1 | 0 | 524.206
8 | Labor | 175 | 1400 | Condenser | 1616.71 | 1.05 | 1697.5455 | 1.07 | 1816.3737 | 1.3 | 2361.2858 | 1 | 300 | 2661.2858
| Following for LEEN  Readings  HVAC |  | 4991.5393 | Line Set | 278.01 | 1.05 | 291.9105 | 1.07 | 312.3442 | 1.3 | 406.0475 | 1 | 0 | 406.0475
| “Replacement (New) Central AC/Air Source Heat Pump Capacity (BTUs)” = 24,000 |  |  |  | 2253.63 | [7 empty] | Total less LABOR | 3591.5393
“Replacement (New) Central AC/Air Source Heat Pump – SEER” = 16
“Replacement (New) Central AC/Air Source Heat Pump – EER” = 14
MODEL NUMBER SPECIFIC = CAPF1824B
| A/C COIL-CONDENSER-LINE SET |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | GOODMAN 16 SEER, 2.5-ton R410A, GSX160301, ¾ Line Set | 3807.2479 | 3807.2479 | Coil | 448.91 | 1.05 | 471.3555 | 1.07 | 504.3504 | 1.3 | 655.6555 | 1 | 0 | 655.6555
8 | Labor | 175 | 1400 | Condenser | 1674.4 | 1.05 | 1758.12 | 1.07 | 1881.1884 | 1.3 | 2445.5449 | 1 | 300 | 2745.5449
| Following for LEEN  Readings  HVAC |  | 5207.2479 | Line Set | 278.01 | 1.05 | 291.9105 | 1.07 | 312.3442 | 1.3 | 406.0475 | 1 | 0 | 406.0475
| “Replacement (New) Central AC/Air Source Heat Pump Capacity (BTUs)” = 30,000 |  |  |  | 2401.32 | [7 empty] | Total less LABOR | 3807.2479
“Replacement (New) Central AC/Air Source Heat Pump – SEER” = 16
“Replacement (New) Central AC/Air Source Heat Pump – EER” = 14
MODEL NUMBER SPECIFIC = CAPF1824B
| A/C COIL-CONDENSER-LINE SET |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | GOODMAN 16 SEER, 3-ton R410A, GSX160361, ¾ Line Set | 4107.7269 | 4107.7269 | Coil | 502.69 | 1.05 | 527.8245 | 1.07 | 564.7722 | 1.3 | 734.2039 | 1 | 0 | 734.2039
8 | Labor | 175 | 1400 | Condenser | 1826.35 | 1.05 | 1917.6675 | 1.07 | 2051.9042 | 1.3 | 2667.4755 | 1 | 300 | 2967.4755
| Following for LEEN  Readings  HVAC |  | 5507.7269 | Line Set | 278.01 | 1.05 | 291.9105 | 1.07 | 312.3442 | 1.3 | 406.0475 | 1 | 0 | 406.0475
| “Replacement (New) Central AC/Air Source Heat Pump Capacity (BTUs)” = 36,000 | [11 empty] | Total less LABOR | 4107.7269
“Replacement (New) Central AC/Air Source Heat Pump – SEER” = 16
“Replacement (New) Central AC/Air Source Heat Pump – EER” = 14
MODEL NUMBER SPECIFIC = CAPF3636B6
RHEEM / RUUD A/C SYSTEMS
| A/C COIL-CONDENSER-LINE SET |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | RHEEM/RUUD 16, SEER 1.5-ton R410A, RA1624, ¾ Line Set | 4542.4158 | 4542.4158 | Coil | 722.32 | 1.05 | 758.436 | 1.07 | 811.5265 | 1.3 | 1054.9845 | 1 | 0 | 1054.9845
8 | Labor | 175 | 1400 | Condenser | 1622.35 | 1.05 | 1703.4675 | 1.07 | 1822.7102 | 1.3 | 2369.5233 | 1 | 300 | 2669.5233
| Following for LEEN  Readings  HVAC |  | 5942.4158 | Line Set | 560 | 1.05 | 588 | 1.07 | 629.16 | 1.3 | 817.908 | 1 | 0 | 817.908
| “Replacement (New) Central AC/Air Source Heat Pump Capacity (BTUs)” = 18,000 | [12 empty] | 4542.4158
“Replacement (New) Central AC/Air Source Heat Pump – SEER” = 16
“Replacement (New) Central AC/Air Source Heat Pump – EER” = 14
MODEL NUMBER SPECIFIC = RA1618AJ1NA
| A/C COIL-CONDENSER-LINE SET |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | RHEEM/RUUD 16 SEER, 2-ton R410A, RA1624, ¾ Line Set | 4622.3517 | 4622.3517 | Coil | 722.32 | 1.05 | 758.436 | 1.07 | 811.5265 | 1.3 | 1054.9845 | 1 | 0 | 1054.9845
8 | Labor | 175 | 1400 | Condenser | 1677.08 | 1.05 | 1760.934 | 1.07 | 1884.1994 | 1.3 | 2449.4592 | 1 | 300 | 2749.4592
| Following for LEEN  Readings  HVAC |  | 6022.3517 | Line Set | 560 | 1.05 | 588 | 1.07 | 629.16 | 1.3 | 817.908 | 1 | 0 | 817.908
| “Replacement (New) Central AC/Air Source Heat Pump Capacity (BTUs)” = 24,000 | [12 empty] | 4622.3517
“Replacement (New) Central AC/Air Source Heat Pump – SEER” = 16
“Replacement (New) Central AC/Air Source Heat Pump – EER” = 14
MODEL NUMBER SPECIFIC = RCF2417HTAMCA
| A/C COIL-CONDENSER-LINE SET |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | RHEEM/RUUD 16 SEER, 2.5-ton R410A, RA1624, ¾ Line Set | 5187.8182 | 5187.8182 | Coil | 722.32 | 1.05 | 758.436 | 1.07 | 811.5265 | 1.3 | 1054.9845 | 1 | 0 | 1054.9845
8 | Labor | 175 | 1400 | Condenser | 2064.24 | 1.05 | 2167.452 | 1.07 | 2319.1736 | 1.3 | 3014.9257 | 1 | 300 | 3314.9257
| Following for LEEN  Readings  HVAC |  | 6587.8182 | Line Set | 560 | 1.05 | 588 | 1.07 | 629.16 | 1.3 | 817.908 | 1 | 0 | 817.908
| “Replacement (New) Central AC/Air Source Heat Pump Capacity (BTUs)” = 30,000 | [12 empty] | 5187.8182
“Replacement (New) Central AC/Air Source Heat Pump – SEER” = 16
“Replacement (New) Central AC/Air Source Heat Pump – EER” = 14
MODEL NUMBER SPECIFIC = RA1630AJ1NA
| A/C CONDENSER-AIR HANDLER-LINE SET |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | RHEEM/RUUD 16 SEER, 3-ton R410A, AJ1NA | 3376.4295 | 3376.4295 | Condenser | 2106.35 | 1.05 | 2211.6675 | 1.07 | 2366.4842 | 1.3 | 3076.4295 | 1 | 300 | 3376.4295
1 | Air Handler and Components | 1698.0861 | 1698.0861 | Air Handler * | 1025.7 | 1.05 | 1076.985 | 1.07 | 1152.3739 | 1.3 | 1498.0861 | 1 | 200 | 1698.0861
1 | ¾ Line Set | 408.954 | 408.954 | Line Set | 280 | 1.05 | 294 | 1.07 | 314.58 | 1.3 | 408.954 | 1 | 0 | 408.954
16 | Labor for two men | 175 | 2800 | [10 empty] | 5483.4696
| Following for LEEN  Readings  HVAC |  | 8283.4696 |  | * Air Handler Components
| “Replacement (New) Central AC/Air Source Heat Pump Capacity (BTUs)” = 36,000 |  | 0 |  | 986.05 | Air Handler
| “Replacement (New) Central AC/Air Source Heat Pump – SEER” = 16 |  | 0 |  | 26.44 | ¾ WHIP
| “Replacement (New) Central AC/Air Source Heat Pump – EER” = 14 |  | 0 |  | 2.22 | ¾ PVC
|  |  | 0 |  | 6.76 | ¾ Poly Adapter
|  |  | 0 |  | 4.23 | Hose Clamp
|  |  | 0 |  | 1025.7
0
Combined Descriptions
Needs new A/C system: 9999 ton, R410A condenser. The existing unit uses R22, but is not working at all. Following is the replacement proposal you requested for an air conditioning unit for the house. To replace the unit, must: shut off the furnace; shut off power; disconnect the whip; evacuate any remaining coolant in the old unit; disconnect the coolant line to the condenser; disconnect a-coil from the house duct work; remove old a-coil; remove old condenser; install new condenser; install replacement a-coil; adjust transition piece to the house duct work as necessary; install replacement condenser refrigeration line; charge the condenser with refrigerant; turn on power to the furnace; turn on power to the condenser; test; check for leaks; set for normal operation.
END

## Aquastat
AQUASTAT
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| AQUASTAT |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Aqustat | 165 | 215 | 434.3145 | 434.3145 | Aquastat | 263.13 | 1.05 | 276.2865 | 1.07 | 295.6266 | 1.3 | 384.3145 | 1 | 50 | 434.3145
2 | Labor |  |  | 175 | 350 | Aquastat | 239.21 | [7 empty] | Total less LABOR | 434.3145
784.3145
Description
The aquastat on the boiler has failed and must be replaced. To do this, must: shut off the boiler; drain down the boiler; remove the expansion tank; remove the failing aquastat; install the replacement aquastat; re-install the expansion tank; re-fill the boiler; bleed the system; set for normal operation.
END

## BOILER - HYDRONIC
HYDRONIC BOILER – 85%
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
BUDERUS HYDRONIC BOILERS
| BOILER – HYDRONIC |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Buderus: M/N GC124/3II; 74,000BTU; AFUE 85% |  |  | 2918.0359 | 2918.0359 | Boiler | 1792.5 | 1.05 | 1882.125 | 1.07 | 2013.8737 | 1.3 | 2618.0359 | 1 | 300 | 2918.0359
1 | Materials |  |  | 1684.7792 | 1684.7792 | Materials | 1211.2 | 1 | 1211.2 | 1.07 | 1295.984 | 1.3 | 1684.7792 | 1 | 0 | 1684.7792
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 394.3485 | 394.3485 | Dlvry & Haul | 283.5 | 1 | 283.5 | 1.07 | 303.345 | 1.3 | 394.3485 | 1 | 0 | 394.3485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
| EXPANSION TANK | [13 empty] | Total less LABOR | 5782.1745
1 | Expansion Tank |  |  | 86.2698 | 86.2698
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532 |  | BUDERUS | BTU IN | COST | AFUE | Flue Min.
1 | Labor |  |  | 175 | 175 |  | GC124/3II | 74000 | 1792.5 | 85% | 5”
BACK FLOW PREVENTER
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175
5” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN
1 | Material |  |  | 162.39 | 162.39
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 1792.5
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Hydronic Boiler ● EO $730 ● |  |  | 485 | 485
1 | Permit Chimney Liner |  |  | 125 | 125
11755.9524
| BOILER – HYDRONIC |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Buderus: M/N GC124/4II; 103,000BTU; AFUE 85% |  |  | 3143.6908 | 3143.6908 | Boiler | 1947 | 1.05 | 2044.35 | 1.07 | 2187.4545 | 1.3 | 2843.6908 | 1 | 300 | 3143.6908
1 | Materials |  |  | 1684.7792 | 1684.7792 | Materials | 1211.2 | 1 | 1211.2 | 1.07 | 1295.984 | 1.3 | 1684.7792 | 1 | 0 | 1684.7792
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 394.3485 | 394.3485 | Dlvry & Haul | 283.5 | 1 | 283.5 | 1.07 | 303.345 | 1.3 | 394.3485 | 1 | 0 | 394.3485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
| EXPANSION TANK | [13 empty] | Total less LABOR | 6007.8294
1 | Expansion Tank |  |  | 86.2698 | 86.2698
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532 |  | BUDERUS | BTU IN | COST | AFUE | Flue Min.
1 | Labor |  |  | 175 | 175 |  | GC124/4II | 103000 | 1947 | 85% | 5”
BACK FLOW PREVENTER
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175
5” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN
1 | Material |  |  | 162.39 | 162.39
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 1947
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Hydronic Boiler ● EO $730 ● |  |  | 485 | 485
1 | Permit Chimney Liner |  |  | 125 | 125
11981.6074
| BOILER – HYDRONIC |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Buderus: M/N GC124/5II; 132,000BTU; AFUE 85% |  |  | 3521.6082 | 3521.6082 | Boiler | 2205.75 | 1.05 | 2316.0375 | 1.07 | 2478.1601 | 1.3 | 3221.6082 | 1 | 300 | 3521.6082
1 | Materials |  |  | 1684.7792 | 1684.7792 | Materials | 1211.2 | 1 | 1211.2 | 1.07 | 1295.984 | 1.3 | 1684.7792 | 1 | 0 | 1684.7792
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 394.3485 | 394.3485 | Dlvry & Haul | 283.5 | 1 | 283.5 | 1.07 | 303.345 | 1.3 | 394.3485 | 1 | 0 | 394.3485
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 6385.7467
|  132,000/112,200 6”  |  |  |  | 9185.7467
| EXPANSION TANK | [5 empty] | BUDERUS | BTU IN | COST | AFUE | Flue Min.
1 | Expansion Tank |  |  | 86.2698 | 86.2698 |  | GC144/5II | 132000 | 2205.75 | 85% | 6”
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532
1 | Labor |  |  | 175 | 175
296.323
BACK FLOW PREVENTER
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 2205.75
405.065
6” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN
1 | Material |  |  | 162.39 | 162.39
1 | Labor |  |  | 175 | 175
337.39
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
| BOILER – HYDRONIC |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Buderus: M/N G234X/38; 160,000BTU; AFUE 85% |  |  | 4013.4484 | 4013.4484 | Boiler | 2542.5 | 1.05 | 2669.625 | 1.07 | 2856.4988 | 1.3 | 3713.4484 | 1 | 300 | 4013.4484
1 | Materials |  |  | 1684.7792 | 1684.7792 | Materials | 1211.2 | 1 | 1211.2 | 1.07 | 1295.984 | 1.3 | 1684.7792 | 1 | 0 | 1684.7792
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 394.3485 | 394.3485 | Dlvry & Haul | 283.5 | 1 | 283.5 | 1.07 | 303.345 | 1.3 | 394.3485 | 1 | 0 | 394.3485
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 6877.587
|  160,000/136,000 7”  |  |  |  | 9677.587
| EXPANSION TANK | [5 empty] | BUDERUS | BTU IN | COST | AFUE | Flue Min.
1 | Expansion Tank |  |  | 86.2698 | 86.2698 |  | G234X/38 | 160000 | 2542.5 | 85% | 7”
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532
1 | Labor |  |  | 175 | 175
296.323
BACK FLOW PREVENTER
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 2542.5
405.065
7” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN
1 | Material |  |  | 192.88 | 192.88
1 | Labor |  |  | 175 | 175
367.88
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
| BOILER – HYDRONIC |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Buderus: M/N G234X/45; 187,000BTU; AFUE 85% |  |  | 4420.9418 | 4420.9418 | Boiler | 2821.5 | 1.05 | 2962.575 | 1.07 | 3169.9552 | 1.3 | 4120.9418 | 1 | 300 | 4420.9418
1 | Materials |  |  | 1684.7792 | 1684.7792 | Materials | 1211.2 | 1 | 1211.2 | 1.07 | 1295.984 | 1.3 | 1684.7792 | 1 | 0 | 1684.7792
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 394.3485 | 394.3485 | Dlvry & Haul | 283.5 | 1 | 283.5 | 1.07 | 303.345 | 1.3 | 394.3485 | 1 | 0 | 394.3485
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 7285.0804
|  187,000/158,950 7”  |  |  |  | 10085.0804
| EXPANSION TANK | [5 empty] | BUDERUS | BTU IN | COST | AFUE | Flue Min.
1 | Expansion Tank |  |  | 86.2698 | 86.2698 |  | G234X/45 | 187000 | 2821.5 | 85% | 7”
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532
1 | Labor |  |  | 175 | 175
296.323
BACK FLOW PREVENTER
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 2821.5
405.065
7” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN
1 | Material |  |  | 192.88 | 192.88
1 | Labor |  |  | 175 | 175
367.88
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
| BOILER – HYDRONIC |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Buderus: M/N G234X/55; 228,000BTU; AFUE 85% |  |  | 4723.5324 | 4723.5324 | Boiler | 3028.6758 | 1.05 | 3180.1096 | 1.07 | 3402.7173 | 1.3 | 4423.5324 | 1 | 300 | 4723.5324
1 | Materials |  |  | 1684.7792 | 1684.7792 | Materials | 1211.2 | 1 | 1211.2 | 1.07 | 1295.984 | 1.3 | 1684.7792 | 1 | 0 | 1684.7792
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 394.3485 | 394.3485 | Dlvry & Haul | 283.5 | 1 | 283.5 | 1.07 | 303.345 | 1.3 | 394.3485 | 1 | 0 | 394.3485
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 7587.671
|  228,000/194,000 7”  |  |  |  | 10387.671
| EXPANSION TANK |  |  |  | 0 |  | BUDERUS | BTU IN | COST | AFUE | Flue Min.
1 | Expansion Tank |  |  | 86.2698 | 86.2698 |  | G234X/55 | 228000 | 3028.6758 | 85% | 7”
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532
1 | Labor |  |  | 175 | 175
296.323
BACK FLOW PREVENTER
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 3028.6758
405.065
7” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN
1 | Material |  |  | 192.88 | 192.88
1 | Labor |  |  | 175 | 175
367.88
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
| BOILER – HYDRONIC |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Buderus: M/N G234X/64; 266,000BTU; AFUE 85% |  |  | 4723.5324 | 4723.5324 | Boiler | 3028.6758 | 1.05 | 3180.1096 | 1.07 | 3402.7173 | 1.3 | 4423.5324 | 1 | 300 | 4723.5324
1 | Materials |  |  | 1684.7792 | 1684.7792 | Materials | 1211.2 | 1 | 1211.2 | 1.07 | 1295.984 | 1.3 | 1684.7792 | 1 | 0 | 1684.7792
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 394.3485 | 394.3485 | Dlvry & Haul | 283.5 | 1 | 283.5 | 1.07 | 303.345 | 1.3 | 394.3485 | 1 | 0 | 394.3485
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 7587.671
|  266,000/226,000 8”  |  |  |  | 10387.671
| EXPANSION TANK |  |  |  | 0 |  | BUDERUS | BTU IN | COST | AFUE | Flue Min.
1 | Expansion Tank |  |  | 86.2698 | 86.2698 |  | G234X/64 | 266000 | 3028.6758 | 85% | 8”
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532
1 | Labor |  |  | 175 | 175
296.323
BACK FLOW PREVENTER
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 3028.6758
405.065
7” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN
1 | Material |  |  | 192.88 | 192.88
1 | Labor |  |  | 175 | 175
367.88
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
BRADFORD WHITE HYDRONIC BOILERS
| BOILER – HYDRONIC |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White: M/N BMFTHW140NA1XN; 140,000 BTU; AFUE 95% |  |  | 3978.6727 | 3978.6727 | Boiler | 2518.69 | 1.05 | 2644.6245 | 1.07 | 2829.7482 | 1.3 | 3678.6727 | 1 | 300 | 3978.6727
1 | Materials |  |  | 1684.7792 | 1684.7792 | Materials | 1211.2 | 1 | 1211.2 | 1.07 | 1295.984 | 1.3 | 1684.7792 | 1 | 0 | 1684.7792
1 | PVC concentric vent with termination kit and piping |  |  | 457.0965 | 457.0965 | Concentric Kit | 328.61 | 1 | 328.61 | 1.07 | 351.6127 | 1.3 | 457.0965 | 1 | 0 | 457.0965
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 7175.5663
9975.5663
| BACK FLOW PREVENTER |  |  |  | 0 |  | Bradford White | BTU IN | COST | AFUE | Flue Min.
1 | Back Flow Preventer |  |  | 230.065 | 230.065 |  | BMF…..140 | 140000 | 2518.69 | 93% | 5”
1 | Labor |  |  | 175 | 175
405.065
5” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN
1 | Material |  |  | 162.39 | 162.39
1 | Labor |  |  | 175 | 175
[5 empty] | 337.39 |  |  | AVERAGE | 2518.69
NEUTRALIZER CONDENSATE PUMP
1 | Pump | 165 | 215 | 247.5 | 247.5
2 | Labor |  |  | 175 | 350
597.5
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
Hydronic Description
To do this we must: shut off gas; shut off water; disconnect water line connection; disconnect gas line connection; drain down boiler; disconnect from house line; remove old boiler; install replacement boiler; connect to house line; connect to water line; fill boiler; test for water leaks; connect to gas line; test for gas leaks; commission boiler and bleed house lines; set for normal operation. This will also require a chimney liner.
Indirect DHW Description
INDIRECT DHW | The Indirect DHW for the hydronic boiler is leaking and must be replaced. To do this, must: shut off the boiler; shut off the water; drain down the house line connections; drain down the boiler; drain down the faulty Indirect DHW; disconnect the water lines from the boiler; disconnect the house water lines; remove the existing Indirect DHW; place the new Indirect DHW; repipe copper lines to the Indirect DHW including the house water lines, lines to and from the hydronic boiler; fill the hydronic boiler and the Indirect DHW; bleed the boiler; bleed the Indirect DHW; check for water leaks; turn on the gas; check for gas leaks; re-commission the hydronic boiler; set for normal operation.
HYDRONIC BOILER – 90%+ – Condensing
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| BOILER HYDRONIC-Condensing |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GWC-070-W; 070,000BTU; AFUE 91% |  |  | 4340.7576 | 4340.7576 | Boiler | 2766.6 | 1.05 | 2904.93 | 1.07 | 3108.2751 | 1.3 | 4040.7576 | 1 | 300 | 4340.7576
1 | Materials |  |  | 1762.0771 | 1762.0771 | Materials | 1266.77 | 1 | 1266.77 | 1.07 | 1355.4439 | 1.3 | 1762.0771 | 1 | 0 | 1762.0771
1 | Electrical hook up |  |  | 299.9831 | 299.9831 | Elec Hook Up | 215.66 | 1 | 215.66 | 1.07 | 230.7562 | 1.3 | 299.9831 | 1 | 0 | 299.9831
1 | Delivery and Haul Away |  |  | 265.834 | 265.834 | Dlvry & Haul | 191.11 | 1 | 191.11 | 1.07 | 204.4877 | 1.3 | 265.834 | 1 | 0 | 265.834
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 7153.6518
|  70,000/63,700  |  |  |  | 9953.6518 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
[5 empty] | 0 |  | GWC-070-W | 70000 | 2766.6 | 90% | 5”
0
0
0
0
0
[5 empty] | 0 |  |  | AVERAGE | 2766.6
0
| BOILER HYDRONIC-Condensing |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GWC-105-W; 105,000BTU; AFUE 91% |  |  | 4622.0011 | 4622.0011 | Boiler | 2959.16 | 1.05 | 3107.118 | 1.07 | 3324.6163 | 1.3 | 4322.0011 | 1 | 300 | 4622.0011
1 | Materials |  |  | 1762.0771 | 1762.0771 | Materials | 1266.77 | 1 | 1266.77 | 1.07 | 1355.4439 | 1.3 | 1762.0771 | 1 | 0 | 1762.0771
1 | Electrical hook up |  |  | 299.9831 | 299.9831 | Elec Hook Up | 215.66 | 1 | 215.66 | 1.07 | 230.7562 | 1.3 | 299.9831 | 1 | 0 | 299.9831
1 | Delivery and Haul Away |  |  | 265.834 | 265.834 | Dlvry & Haul | 191.11 | 1 | 191.11 | 1.07 | 204.4877 | 1.3 | 265.834 | 1 | 0 | 265.834
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 7434.8953
|  105,000/95,550  |  |  |  | 10234.8953 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
[5 empty] | 0 |  | GWC-105-W | 100000 | 2959.16 | 90% | 5”
0
0
0
0
0
[5 empty] | 0 |  |  | AVERAGE | 2959.16
0
| BOILER HYDRONIC-Condensing |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GWC-140-W; 140,000BTU; AFUE 91% |  |  | 5284.4482 | 5284.4482 | Boiler | 3412.72 | 1.05 | 3583.356 | 1.07 | 3834.1909 | 1.3 | 4984.4482 | 1 | 300 | 5284.4482
1 | Materials |  |  | 1762.0771 | 1762.0771 | Materials | 1266.77 | 1 | 1266.77 | 1.07 | 1355.4439 | 1.3 | 1762.0771 | 1 | 0 | 1762.0771
1 | Electrical hook up |  |  | 299.9831 | 299.9831 | Elec Hook Up | 215.66 | 1 | 215.66 | 1.07 | 230.7562 | 1.3 | 299.9831 | 1 | 0 | 299.9831
1 | Delivery and Haul Away |  |  | 265.834 | 265.834 | Dlvry & Haul | 191.11 | 1 | 191.11 | 1.07 | 204.4877 | 1.3 | 265.834 | 1 | 0 | 265.834
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 8097.3423
|  140,000/125,000  |  |  |  | 10897.3423 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
[5 empty] | 0 |  | GWC-140-W | 140000 | 3412.72 | 90% | 6”
0
0
0
0
0
[5 empty] | 0 |  |  | AVERAGE | 3412.72
0
| BOILER HYDRONIC-Condensing |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GWC-175-W; 175,000BTU; AFUE 91% |  |  | 5935.0356 | 5935.0356 | Boiler | 3858.16 | 1.05 | 4051.068 | 1.07 | 4334.6428 | 1.3 | 5635.0356 | 1 | 300 | 5935.0356
1 | Materials |  |  | 1762.0771 | 1762.0771 | Materials | 1266.77 | 1 | 1266.77 | 1.07 | 1355.4439 | 1.3 | 1762.0771 | 1 | 0 | 1762.0771
1 | Electrical hook up |  |  | 299.9831 | 299.9831 | Elec Hook Up | 215.66 | 1 | 215.66 | 1.07 | 230.7562 | 1.3 | 299.9831 | 1 | 0 | 299.9831
1 | Delivery and Haul Away |  |  | 265.834 | 265.834 | Dlvry & Haul | 191.11 | 1 | 191.11 | 1.07 | 204.4877 | 1.3 | 265.834 | 1 | 0 | 265.834
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 8747.9297
|  175,000/150,000  |  |  |  | 11547.9297 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
[5 empty] | 0 |  | GWC-175-W | 175000 | 3858.16 | 90% | 6”
0
0
0
0
0
[5 empty] | 0 |  |  | AVERAGE | 3858.16
0
| DHW - INDIRECT |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GL-42-W 39gal Indirect |  |  | 1437.4763 | 1437.4763 | ID-DHW | 778.8 | 1.05 | 817.74 | 1.07 | 874.9818 | 1.3 | 1137.4763 | 1 | 300 | 1437.4763
1 | Pipe and fittings |  |  | 496.0723 | 496.0723 | Pipe & Fittings | 356.63 | 1 | 356.63 | 1.07 | 381.5941 | 1.3 | 496.0723 | 1 | 0 | 496.0723
4 | Labor for two men at 8 hours each man |  |  | 175 | 700 | Elec Hook Up | 0 | 1 | 0 | 1.07 | 0 | 1.3 | 0 | 1 | 0 | 0
[5 empty] | 2633.5487 | Dlvry & Haul | 0 | 1 | 0 | 1.07 | 0 | 1.3 | 0 | 1 | 0 | 0
[6 empty] | Permit | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0
[15 empty] | Total less LABOR | 1933.5487
[7 empty] | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
[7 empty] | GL-42-W |  | 778.8
[8 empty] | AVERAGE | 778.8
| DHW - INDIRECT |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson DHW: GL-53-W 53gal Indirect |  |  | 1625.011 | 1625.011 | ID-DHW | 907.2 | 1.05 | 952.56 | 1.07 | 1019.2392 | 1.3 | 1325.011 | 1 | 300 | 1625.011
1 | Pipe and fittings |  |  | 520.8759 | 520.8759 | Pipe & Fittings | 356.63 | 1.05 | 374.4615 | 1.07 | 400.6738 | 1.3 | 520.8759 | 1 | 0 | 520.8759
4 | Labor for two men at 8 hours each man |  |  | 175 | 700 | Elec Hook Up | 0 | 1.05 | 0 | 1.07 | 0 | 1.3 | 0 | 1 | 0 | 0
[5 empty] | 2845.8869 | Dlvry & Haul | 0 | 1.05 | 0 | 1.07 | 0 | 1.3 | 0 | 1 | 0 | 0
[6 empty] | Permit | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0
[15 empty] | Total less LABOR | 2145.8869
[7 empty] | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
[7 empty] | GL-53-W |  | 907.2
[8 empty] | AVERAGE | 907.2
Hydronic Description with Embedded Liner
The chimney has an embedded liner and won’t come out. Need proposal for 90+ boiler to solve the problem. To do this, must: shut off gas; shut off water; disconnect water line connection; disconnect gas line connection; drain down boiler; disconnect from house line; remove old boiler; install replacement boiler; core drill through foundation for PVC piping; connect to house line; connect to water line; fill boiler; test for water leaks; connect to gas line; test for gas leaks; commission boiler and bleed house lines; set for normal operation.
END

## Expansion Tank
EXPANSION TANK
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| EXPANSION TANK |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Expansion Tank | 165 | 215 | 86.2698 | 86.2698 | Exp Tnk | 62.02 | 1 | 62.02 | 1.07 | 66.3614 | 1.3 | 86.2698 | 1 | 0 | 86.2698
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532 | Tee | 25.2 | 1 | 25.2 | 1.07 | 26.964 | 1.3 | 35.0532 | 1 | 0 | 35.0532
1 | Labor |  |  | 175 | 175 | Ball Valve | 20.86 | 1 | 20.86 | 1.07 | 22.3202 | 1.3 | 29.0163 | 1 | 0 | 29.0163
[5 empty] | 296.323 | [9 empty] | Total less LABOR | 150.3393
Description
Must shut down boiler; drain down boiler; remove old expansion tank and connections; install new expansion tank and connections; refill boiler; bleed system; test boiler; set for normal operation.
END

## Zone Valves
ZONE VALVES
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| ZONE VALVES |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Materials – zone valves |  |  | 185.78 | 185.78 | Zone valve | 116.6 | 1 | 116.6 | 1.07 | 124.762 | 1.3 | 162.1906 | 1 | 0 | 162.1906
1 | Labor |  |  | 175 | 175 | Zone valve | 106 | [7 empty] | Total less LABOR | 162.1906
360.78
END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END

## BOILER - STEAM
STEAM BOILERS – 83%
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| BOILER – STEAM |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GSA-075 NIPW; 075,000BTU; AFUE 83% |  |  | 2871.7364 | 2871.7364 | Boiler | 1760.8 | 1.05 | 1848.84 | 1.07 | 1978.2588 | 1.3 | 2571.7364 | 1 | 300 | 2871.7364
1 | Materials |  |  | 2018.341 | 2018.341 | Materials | 1451 | 1 | 1451 | 1.07 | 1552.57 | 1.3 | 2018.341 | 1 | 0 | 2018.341
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 5945.0953
|  75,000/62,250 5”  |  |  |  | 8745.0953
| BACK FLOW PREVENTER |  |  |  | 0 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
1 | Back Flow Preventer |  |  | 230.065 | 230.065 |  | GSA-075 | 75000 | 1760.8 | 83% | 5”
1 | Labor |  |  | 175 | 175
405.065
| AUTO WATER FEED |  |  |  | 0
1 | Material |  |  | 398.8628 | 398.8628
1 | Labor |  |  | 175 | 175
[5 empty] | 573.8628 |  |  | AVERAGE | 1760.8
5” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN
1 | Material |  |  | 162.39 | 162.39
1 | Labor |  |  | 175 | 175
337.39
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
| BOILER – STEAM |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GSA-100 NIPW; 100,000BTU; AFUE 83% |  |  | 2944.6325 | 2944.6325 | Boiler | 1810.71 | 1.05 | 1901.2455 | 1.07 | 2034.3327 | 1.3 | 2644.6325 | 1 | 300 | 2944.6325
1 | Materials |  |  | 2018.341 | 2018.341 | Materials | 1451 | 1 | 1451 | 1.07 | 1552.57 | 1.3 | 2018.341 | 1 | 0 | 2018.341
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 6017.9914
|  100,000/83,000 5”  |  |  |  | 8817.9914
| BACK FLOW PREVENTER |  |  |  | 0 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
1 | Back Flow Preventer |  |  | 230.065 | 230.065 |  | GSA-100 | 100000 | 1810.71 | 83% | 5”
1 | Labor |  |  | 175 | 175
405.065
| AUTO WATER FEED |  |  |  | 0
1 | Material |  |  | 398.8628 | 398.8628
1 | Labor |  |  | 175 | 175
[5 empty] | 573.8628 |  |  | AVERAGE | 1810.71
5” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN
1 | Material |  |  | 162.39 | 162.39
1 | Labor |  |  | 175 | 175
337.39
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
| BOILER – STEAM |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GSA-125 NIPW; 125,000BTU; AFUE 83% |  |  | 3551.1113 | 3551.1113 | Boiler | 2225.95 | 1.05 | 2337.2475 | 1.07 | 2500.8548 | 1.3 | 3251.1113 | 1 | 300 | 3551.1113
1 | Materials |  |  | 2018.341 | 2018.341 | Materials | 1451 | 1 | 1451 | 1.07 | 1552.57 | 1.3 | 2018.341 | 1 | 0 | 2018.341
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 6624.4702
|  125,000/103,750 6”  |  |  |  | 9424.4702
| BACK FLOW PREVENTER |  |  |  | 0 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
1 | Back Flow Preventer |  |  | 230.065 | 230.065 |  | GSA-125 | 125000 | 2225.95 | 83% | 6”
1 | Labor |  |  | 175 | 175
405.065
| AUTO WATER FEED |  |  |  | 0
1 | Material |  |  | 398.8628 | 398.8628
1 | Labor |  |  | 175 | 175
[5 empty] | 573.8628 |  |  | AVERAGE | 2225.95
6” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN
1 | Material |  |  | 162.39 | 162.39
1 | Labor |  |  | 175 | 175
337.39
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| ADD $1,000 for clack-out. |  |  |  | 2135
| BOILER – STEAM |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GSA-150 NIPW; 150,000BTU; AFUE 83% |  |  | 3741.9029 | 3741.9029 | Boiler | 2356.58 | 1.05 | 2474.409 | 1.07 | 2647.6176 | 1.3 | 3441.9029 | 1 | 300 | 3741.9029
1 | Materials |  |  | 2018.341 | 2018.341 | Materials | 1451 | 1 | 1451 | 1.07 | 1552.57 | 1.3 | 2018.341 | 1 | 0 | 2018.341
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 6815.2618
|  150,000/124,500 6”  |  |  |  | 9615.2618
| BACK FLOW PREVENTER |  |  |  | 0 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
1 | Back Flow Preventer |  |  | 230.065 | 230.065 |  | GSA-150 | 150000 | 2356.58 | 83% | 6”
1 | Labor |  |  | 175 | 175
405.065
| AUTO WATER FEED |  |  |  | 0
1 | Material |  |  | 398.8628 | 398.8628
1 | Labor |  |  | 175 | 175
[5 empty] | 573.8628 |  |  | AVERAGE | 2356.58
6” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN
1 | Material |  |  | 162.39 | 162.39
1 | Labor |  |  | 175 | 175
337.39
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| ADD $1,000 for clack-out. |  |  |  | 2135
| BOILER – STEAM |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GSA-175 NIPW; 175,000BTU; AFUE 83% |  |  | 3655.044 | 3655.044 | Boiler | 2297.11 | 1.05 | 2411.9655 | 1.07 | 2580.8031 | 1.3 | 3355.044 | 1 | 300 | 3655.044
1 | Materials |  |  | 2018.341 | 2018.341 | Materials | 1451 | 1 | 1451 | 1.07 | 1552.57 | 1.3 | 2018.341 | 1 | 0 | 2018.341
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 6728.4029
|  175,000/145,250 7”  |  |  |  | 9528.4029
| BACK FLOW PREVENTER |  |  |  | 0 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
1 | Back Flow Preventer |  |  | 230.065 | 230.065 |  | GSA-175 | 175000 | 2297.11 | 83% | 7”
1 | Labor |  |  | 175 | 175
405.065
| AUTO WATER FEED |  |  |  | 0
1 | Material |  |  | 398.8628 | 398.8628
1 | Labor |  |  | 175 | 175
[5 empty] | 573.8628 |  |  | AVERAGE | 2297.11
7” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN
1 | Material |  |  | 192.88 | 192.88
1 | Labor |  |  | 175 | 175
367.88
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
| BOILER – STEAM |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GSA-200 NIPW; 200,000BTU; AFUE 83% |  |  | 3957.5093 | 3957.5093 | Boiler | 2504.2 | 1.05 | 2629.41 | 1.07 | 2813.4687 | 1.3 | 3657.5093 | 1 | 300 | 3957.5093
1 | Materials |  |  | 2018.341 | 2018.341 | Materials | 1451 | 1 | 1451 | 1.07 | 1552.57 | 1.3 | 2018.341 | 1 | 0 | 2018.341
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man |  |  | 175 | 2800 | [9 empty] | Total less LABOR | 7030.8682
|  200,000/166,000 7”  |  |  |  | 9830.8682
| BACK FLOW PREVENTER |  |  |  | 0 |  | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
1 | Back Flow Preventer |  |  | 230.065 | 230.065 |  | GSA-200 | 200000 | 2504.2 | 83% | 7”
1 | Labor |  |  | 175 | 175
405.065
| AUTO WATER FEED |  |  |  | 0
1 | Material |  |  | 398.8628 | 398.8628
1 | Labor |  |  | 175 | 175
[5 empty] | 573.8628 |  |  | AVERAGE | 2504.2
7” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN
1 | Material |  |  | 192.88 | 192.88
1 | Labor |  |  | 175 | 175
367.88
| CHIMNEY LINER and CAP |  |  |  | 0
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
0
580.0649
| BOILER – STEAM |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GSA-238 NIPW; 238,000BTU; AFUE 83% |  |  | 5029.3193 | 5029.3193 | Boiler | 3238.04 | 1.05 | 3399.942 | 1.07 | 3637.9379 | 1.3 | 4729.3193 | 1 | 300 | 5029.3193
1 | Materials |  |  | 2018.341 | 2018.341 | Materials | 1451 | 1 | 1451 | 1.07 | 1552.57 | 1.3 | 2018.341 | 1 | 0 | 2018.341
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
24 | Labor for three men at 8 hours each man |  |  | 175 | 4200 | [9 empty] | Total less LABOR | 8102.6782
|  238,000/197,540 8”  |  |  |  | 12302.6782
[7 empty] | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
| BACK FLOW PREVENTER |  |  |  | 0 |  | GSA-238 | 238000 | 3238.04 | 83% | 8”
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175
405.065
| AUTO WATER FEED |  |  |  | 0
1 | Material |  |  | 398.8628 | 398.8628
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 3238.04
573.8628
8” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN
1 | Material |  |  | 192.88 | 192.88
1 | Labor |  |  | 175 | 175
367.88
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125
| 0 |  |  |  | 2135
| BOILER – STEAM |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Williamson: M/N GSA-282 NIPW; 282,000BTU; AFUE 83% |  |  | 5586.1686 | 5586.1686 | Boiler | 3619.3 | 1.05 | 3800.265 | 1.07 | 4066.2836 | 1.3 | 5286.1686 | 1 | 300 | 5586.1686
1 | Materials |  |  | 2018.341 | 2018.341 | Materials | 1451 | 1 | 1451 | 1.07 | 1552.57 | 1.3 | 2018.341 | 1 | 0 | 2018.341
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away |  |  | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
24 | Labor for three men at 8 hours each man |  |  | 175 | 4200 | [9 empty] | Total less LABOR | 8659.5275
|  282,000/234,060 8”  |  |  |  | 12859.5275
[7 empty] | WILLIAMSON | BTU IN | COST | AFUE | Flue Min.
| BACK FLOW PREVENTER |  |  |  | 0 |  | GSA-282 | 282000 | 3619.3 | 83% | 8”
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175
405.065
| AUTO WATER FEED |  |  |  | 0
1 | Material |  |  | 398.8628 | 398.8628
1 | Labor |  |  | 175 | 175 |  |  | AVERAGE | 3619.3
573.8628
8” | UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN
1 | Material |  |  | 192.88 | 192.88
1 | Labor |  |  | 175 | 175
367.88
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 1875
1 | Permit Chimney Liner |  |  | 125 | 125
| ADD $1,000 for clack-out. |  |  |  | 2000
Regular Description
Must: shut off gas; shut off water; disconnect water line connection; disconnect gas line connection; drain down boiler; disconnect from header; drain down header of any excess water; remove old boiler; install replacement boiler; connect to header; connect to water line; fill boiler; check for water leaks; make electrical connections; connect to gas line; test for gas leaks; commission boiler; set for normal operation. Also, will have to line the chimney per local code.
Return Steam Line Leak
The return line to the steam boiler is leaking at the point of connection to the boiler block. Over time, the return line has corroded to the point of not being able to be removed. Attempting to do this will crack the boiler block. The boiler must be replaced.
Boiler Drain Valve Leak
There is an active leak at the steam boiler drain valve which has corroded to the boiler block (see picture). This can’t be removed without cracking the boiler block itself. The steam boiler must be replaced.
END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END

## Backflow & Auto Waterfeed
BACK FLOW & WATER FEED
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| BACK FLOW PREVENTER |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Back Flow Preventer | 165 | 215 | 230.065 | 230.065 | Back Flow Prvnt | 129.45 | 1 | 129.45 | 1.07 | 138.5115 | 1.3 | 180.065 | 1 | 50 | 230.065
1 | Labor |  |  | 175 | 175 | Back Flow Prvnt | 117.68 | [7 empty] | Total less LABOR | 230.065
405.065
| AUTO WATER FEED |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Material |  |  | 398.8628 | 398.8628 | Auto Wtr Feed | 250.8 | 1 | 250.8 | 1.07 | 268.356 | 1.3 | 348.8628 | 1 | 50 | 398.8628
1 | Labor |  |  | 175 | 175 | Auto Wtr Feed | 228 | [7 empty] | Total less LABOR | 398.8628
573.8628
Description
Must drain down boiler; remove defective back flow preventer & auto water feed; install new back flow preventer & auto water feed; refill boiler; test boiler; set for normal operation.
END

## DHW - Normal & Short Boy
DHW ATMOSPHERIC
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
STANDARD SIZE DHWs
| 30 GALLON DHW – SPECIAL ORDER ONLY |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG230T6N DHW 30 gallon; .63 efficiency; 9 yr wrnty |  |  | 200 | 200 | DHW | 0 | 1.05 | 0 | 1.07 | 0 | 1.3 | 0 | 1 | 200 | 200
1 | Pipe and fittings |  |  | 175.266 | 175.266 | Pipe & Fittings | 126 | 1 | 126 | 1.07 | 134.82 | 1.3 | 175.266 | 1 | 0 | 175.266
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
3 | Labor |  |  | 175 | 525 |  | 0 | 0 | 0 | 1.07 | 0 | 1.3 | 0 | 0 | 0 | 0
[5 empty] | 1315.266 |  | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  |  |  |  | Pipe & Fittings | 93 | [7 empty] | Total less LABOR | 790.266
1 | Material |  |  | 148.61 | 148.61
1 | Labor |  |  | 175 | 175
323.61
| 40 GALLON DHW |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG240T6N DHW 40 gallon; .63 efficiency; 9 yr wrnty |  |  | 1236.9905 | 1236.9905 | DHW | 710 | 1.05 | 745.5 | 1.07 | 797.685 | 1.3 | 1036.9905 | 1 | 200 | 1236.9905
1 | Pipe and fittings |  |  | 344.2725 | 344.2725 | Pipe & Fittings | 247.5 | 1 | 247.5 | 1.07 | 264.825 | 1.3 | 344.2725 | 1 | 0 | 344.2725
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
3 | Labor |  |  | 175 | 525 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2521.263 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  |  |  |  | Pipe & Fittings | 225 | [7 empty] | Total less LABOR | 1996.263
1 | Material |  |  | 148.61 | 148.61
1 | Labor |  |  | 175 | 175
323.61
| 50 GALLON DHW |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG250T6N DHW: 50 gallon; .63 efficiency; 9 yr wrnty |  |  | 1358.6981 | 1358.6981 | DHW | 793.33 | 1.05 | 832.9965 | 1.07 | 891.3063 | 1.3 | 1158.6981 | 1 | 200 | 1358.6981
1 | Pipe and fittings |  |  | 359.5735 | 359.5735 | Pipe & Fittings | 258.5 | 1 | 258.5 | 1.07 | 276.595 | 1.3 | 359.5735 | 1 | 0 | 359.5735
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
3 | Labor |  |  | 175 | 525 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2658.2716 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  |  |  |  | Pipe & Fittings | 235 | [7 empty] | Total less LABOR | 2133.2716
1 | Material |  |  | 148.61 | 148.61
1 | Labor |  |  | 175 | 175
323.61
| 75 GALLON DHW |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG278H6N DHW: 75 gallon; .63 efficiency; 9 yr wrnty |  |  | 2208.2562 | 2208.2562 | DHW | 1375 | 1.05 | 1443.75 | 1.07 | 1544.8125 | 1.3 | 2008.2562 | 1 | 200 | 2208.2562
1 | Pipe and fittings |  |  | 359.5735 | 359.5735 | Pipe & Fittings | 258.5 | 1 | 258.5 | 1.07 | 276.595 | 1.3 | 359.5735 | 1 | 0 | 359.5735
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
3 | Labor |  |  | 175 | 525 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3507.8297 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  |  |  |  | Pipe & Fittings | 235 | [7 empty] | Total less LABOR | 2982.8297
1 | Material |  |  | 148.61 | 148.61
1 | Labor |  |  | 175 | 175
323.61
SHORT BOY SIZE DHWs
| 40 GALLON SHORT BOY DHW |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG240S6N DHW: 40 gallon short boy; .63 efficiency; 9 yr wrnty |  |  | 1251.596 | 1251.596 | DHW | 720 | 1.05 | 756 | 1.07 | 808.92 | 1.3 | 1051.596 | 1 | 200 | 1251.596
1 | Pipe and fittings |  |  | 344.2725 | 344.2725 | Pipe & Fittings | 247.5 | 1 | 247.5 | 1.07 | 264.825 | 1.3 | 344.2725 | 1 | 0 | 344.2725
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
3 | Labor |  |  | 175 | 525 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2535.8685 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  |  |  |  | Pipe & Fittings | 225 | [7 empty] | Total less LABOR | 2010.8685
1 | Material |  |  | 148.61 | 148.61
1 | Labor |  |  | 175 | 175
323.61
| 50 GALLON SHORT BOY DHW |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG250L6N DHW: 50 gallon short boy; .63 efficiency; 9 yr wrnty |  |  | 1512.8738 | 1512.8738 | DHW | 898.89 | 1.05 | 943.8345 | 1.07 | 1009.9029 | 1.3 | 1312.8738 | 1 | 200 | 1512.8738
1 | Pipe and fittings |  |  | 344.2725 | 344.2725 | Pipe & Fittings | 247.5 | 1 | 247.5 | 1.07 | 264.825 | 1.3 | 344.2725 | 1 | 0 | 344.2725
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
3 | Labor |  |  | 175 | 525 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2797.1463 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  |  |  |  | Pipe & Fittings | 225 | [7 empty] | Total less LABOR | 2272.1463
1 | Material |  |  | 148.61 | 148.61
1 | Labor |  |  | 175 | 175
323.61
DHW Tune and Clean
After a tune and clean, and adjusting the gas control valve, still have flame roll out. Will need a new DHW. To do this we must: shut off water; disconnect water lines; drain DHW; shut off gas; disconnect gas line; disconnect flue pipe; remove existing DHW; install new DHW; connect to water lines; fill DHW; test for water leaks; connect flue pipe; connect to gas line; turn on gas; test for gas leaks; commission DHW; set for normal operation. A short DHW is recommended to gain sufficient pitch.
Downward pitch and complex flue piping
The flue pipe from the DHW to the main that connects to the chimney is downward pitched. It connects to the main flue pipe coming from the steam boiler with a tee. This connection will cause churn. Finally, there is no room to run a flue pipe to the chimney and connect properly because of the distance to the sill. To solve this problem, suggest replacing the existing DHW with a 40 gallon short boy DHW. This will allow the connection to the main flue to be made with a reducer / Y combination. To replace the DHW, must: shut off water; disconnect water lines; drain DHW; shut off gas; disconnect gas line; disconnect flue pipe; remove existing DHW; install new DHW; connect to water lines; fill DHW; test for water leaks; connect flue pipe; connect to gas line; turn on gas; test for gas leaks; commission DHW; set for normal operation. A flue upgrade to 4” is also required per code.
END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END

## DHW - Direct & Power Vent
DHW DIRECT & POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT | DHW POWER VENT
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
POWER VENT DHWs
| DHW POWER VENT |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG1PV40S6N PV DHW: 40 gal; .68 euf; 9-yr wrnty. |  |  | 2244.77 | 2244.77 | DHW | 1400 | 1.05 | 1470 | 1.07 | 1572.9 | 1.3 | 2044.77 | 1 | 200 | 2244.77
1 | Pipe and fittings |  |  | 433.0183 | 433.0183 | Pipe & Fittings | 311.3 | 1 | 311.3 | 1.07 | 333.091 | 1.3 | 433.0183 | 1 | 0 | 433.0183
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
5 | Labor |  |  | 175 | 875 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3967.7883 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Pipe & Fittings | 283 | [7 empty] | Total less LABOR | 3092.7883
| DHW POWER VENT |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG1PV50S*N19 PV DHW: 50 gal; .69 euf; 9-yr wrnty. |  |  | 2475.2156 | 2475.2156 | DHW | 1557.78 | 1.05 | 1635.669 | 1.07 | 1750.1658 | 1.3 | 2275.2156 | 1 | 200 | 2475.2156
1 | Pipe and fittings, upgrade kit |  |  | 789.7402 | 789.7402 | Pipe & Fittings | 567.75 | 1 | 567.75 | 1.07 | 607.4925 | 1.3 | 789.7402 | 1 | 0 | 789.7402
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
5 | Labor |  |  | 175 | 875 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4554.9558 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Pipe & Fittings | 204.6 | [7 empty] | Total less LABOR | 3679.9558
[6 empty] | Upgrade kit | 363.15
| 75 GALLON PV DHW – SPECIAL ORDER ONLY |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG2PV75H6N PV DHW: 75 gal; .63 eff.; 9-yr wrnty. |  |  | 3487.5228 | 3487.5228 | DHW | 2250.88 | 1.05 | 2363.424 | 1.07 | 2528.8637 | 1.3 | 3287.5228 | 1 | 200 | 3487.5228
1 | Pipe and fittings |  |  | 367.683 | 367.683 | Pipe & Fittings | 264.33 | 1 | 264.33 | 1.07 | 282.8331 | 1.3 | 367.683 | 1 | 0 | 367.683
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
5 | Labor |  |  | 175 | 875 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5145.2058 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Pipe & Fittings | 240.3 | [7 empty] | Total less LABOR | 4270.2058
DIRECT VENT DHWs
| DHW DIRECT VENT |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG2DV40S6NFLX DHW: 40 gal; .60 uef; 9-yr wrnty. |  |  | 3054.638 | 3054.638 | DHW | 2052.22 | 1 | 2052.22 | 1.07 | 2195.8754 | 1.3 | 2854.638 | 1 | 200 | 3054.638
1 | Pipe and fittings |  |  | 284.5986 | 284.5986 | Pipe & Fittings | 204.6 | 1 | 204.6 | 1.07 | 218.922 | 1.3 | 284.5986 | 1 | 0 | 284.5986
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
6 | Labor |  |  | 175 | 1050 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4804.2366 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Pipe & Fittings | 186 | [7 empty] | Total less LABOR | 3754.2366
| DHW DIRECT VENT |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White RG2DV50H6NFLX DHW: 50 gal; .64 uef; 9-yr wrnty. |  |  | 3820.8843 | 3820.8843 | DHW | 2603.08 | 1 | 2603.08 | 1.07 | 2785.2956 | 1.3 | 3620.8843 | 1 | 200 | 3820.8843
1 | Pipe and fittings |  |  | 284.5986 | 284.5986 | Pipe & Fittings | 204.6 | 1 | 204.6 | 1.07 | 218.922 | 1.3 | 284.5986 | 1 | 0 | 284.5986
1 | Permit |  |  | 415 | 415 | Permit | 415 | 1 | 415 | 1 | 415 | 1 | 415 | 1 | 0 | 415
6 | Labor |  |  | 175 | 1050 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5570.4829 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Pipe & Fittings | 186 | [7 empty] | Total less LABOR | 4520.4829
DHW Tune and Clean – Also basic description
After a tune and clean, and adjusting the gas control valve, still have flame roll out. Will need a new DHW. Must: shut off water; disconnect water lines; drain DHW; shut off gas; disconnect gas line; remove flue pipe; patch flue pipe hole in chimney; remove existing DHW; install new PV DHW; drill for installing PVC to the outside; install PVC piping; connect to water lines; fill PV DHW; test for water leaks; connect to gas line; make electrical connections; turn on gas; test for gas leaks; commission PV DHW; set for normal operation. A short DHW is recommended to gain sufficient pitch. ----------- By installing a PV DHW, this will eliminate the CAZ. To do this, must: shut off water; disconnect water lines; drain DHW; shut off gas; disconnect gas line; remove flue pipe; patch flue pipe hole in chimney; remove existing DHW; install new PV DHW; drill for installing PVC to the outside; install PVC piping; connect to water lines; fill PV DHW; test for water leaks; connect to gas line; make electrical connections; turn on gas; test for gas leaks; commission PV DHW; set for normal operation. If the PV DHW is not installed, the chimney will have to be lined for the orphaned DHW that would remain.
END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END

## FLUES - LINER - THERMOCRETE
FLUES – LINER – THERMOCRETE | FLUES – LINER – THERMOCRETE | FLUES – LINER – THERMOCRETE | FLUES – LINER – THERMOCRETE | FLUES – LINER – THERMOCRETE | FLUES – LINER – THERMOCRETE
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
FLUE UPGRADES for DHWs
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Material |  |  | 148.61 | 148.61 | Material | 148.61 | 1 | 148.61 | 1 | 148.61 | 1 | 148.61 | 1 | 0 | 148.61
1 | Labor |  |  | 175 | 175 | Materials | 135.1 | [7 empty] | Total less LABOR | 148.61
323.61
FLUE UPGRADES FOR BOILERS ONLY
| UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 5” & 6” AND RUN |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Material |  |  | 162.39 | 162.39 | Material | 94.23 | 1 | 94.23 | 1 | 94.23 | 1 | 94.23 | 1 | 0 | 94.23
1 | Labor |  |  | 175 | 175 |  | 5” & 6” | [7 empty] | Total less LABOR | 94.23
[5 empty] | 337.39 | Materials | 85.66
| UPGRADE BOILER FLUE – CHECK MATERIALS & LABOR 7” & 8” AND RUN |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Material |  |  | 192.88 | 192.88 | Material | 108.43 | 1 | 108.43 | 1 | 108.43 | 1 | 108.43 | 1 | 0 | 108.43
1 | Labor |  |  | 175 | 175 |  | 7” & 8” | [7 empty] | Total less LABOR | 108.43
[5 empty] | 367.88 | Materials | 98.57
CHIMNEY LINER / THERMOCRETE and CAP
| CHIMNEY LINER and CAP |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● |  |  | 2010 | 2010 | Liner | 2010 | 1 | 2010 | 1 | 2010 | 1 | 2010 | 1 | 0 | 2010
1 | Permit Chimney Liner |  |  | 125 | 125 | Permit | 125 | [7 empty] | Total less LABOR | 2010
2135
COMPLETE: top hat, crown, cement, flashing, permit
| THERMOCRETE and CAP |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Thermocrete Lining IRV, TOT, S-ORNG, W-ORNG |  |  | 2940 | 2940 | Thermocrete | 2940 | 1 | 2940 | 1 | 2940 | 1 | 2940 | 1 | 0 | 2940
[5 empty] | 2940 | [9 empty] | Total less LABOR | 2940
Flue Min. | STEAM |  |  | Flue Min. | HYDRONIC
5” | GSA-075 | 75000 |  | 5” | GC144/3 | 74000
5” | GSA-100 | 100000 |  | 5” | GC144/4 | 103000
6” | GSA-125 | 125000 |  | 6” | GC144/5 | 132000
6” | GSA-150 | 150000 |  | 7” | G234X/38 | 160000
7” | GSA-175 | 175000 |  | 7” | G234X/45 | 187000
7” | GSA-200 | 200000 |  | 7” | G234X/55 | 228000
8” | GSA-250 | 250000 |  | 8” | G234X/64 | 266000
8” | GSA-300 | 300000
END | END | END | END | END | END

## FURNACE
FORCED HOT AIR – 96% AFUE – PV / INDUCED | FORCED HOT AIR – 96% AFUE – PV/INDUCED |  | #VALUE!
Quantity | Description | UNIT PRICE | LINE TOTAL
GOODMAN PV FURNACE
| FURNACE – PV |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMSS96 0402BNA; 40,000BTU; AFUE 96% | 1941.147 | 1941.147 | Furnace | 1123.65 | 1.05 | 1179.8325 | 1.07 | 1262.4208 | 1.3 | 1641.147 | 1 | 300 | 1941.147
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1537.9174 | 1537.9174 | Materials | 1105.62 | 1 | 1105.62 | 1.07 | 1183.0134 | 1.3 | 1537.9174 | 1 | 0 | 1537.9174
1 | PVC for Direct Venting | 328.6098 | 328.6098 | PVC | 236.24 | 1 | 236.24 | 1.07 | 252.7768 | 1.3 | 328.6098 | 1 | 0 | 328.6098
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1005.11 | [7 empty] | Total less LABOR | 4862.6922
|  40,000/38,400  |  | 7662.6922
|  |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
|  |  | 0 |  | 0402BNA | 40000 | 1123.65 | 96% | PV | 1021.5
0
0
0
0
0
|  |  | 0 |  |  | AVERAGE | 1123.65
| FURNACE – PV |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMSS96 0603BN; 60,000BTU; AFUE 96% | 2065.8634 | 2065.8634 | Furnace | 1209.04 | 1.05 | 1269.492 | 1.07 | 1358.3564 | 1.3 | 1765.8634 | 1 | 300 | 2065.8634
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1537.9174 | 1537.9174 | Materials | 1105.62 | 1 | 1105.62 | 1.07 | 1183.0134 | 1.3 | 1537.9174 | 1 | 0 | 1537.9174
1 | PVC for Direct Venting | 328.6098 | 328.6098 | PVC | 236.24 | 1 | 236.24 | 1.07 | 252.7768 | 1.3 | 328.6098 | 1 | 0 | 328.6098
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1005.11 | [7 empty] | Total less LABOR | 4987.4085
|  60,000/57,600  |  | 7787.4085
|  |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
|  |  | 0 |  | 0603BN | 60000 | 1209.04 | 96% | PV | 1099.13
0
0
0
0
0
|  |  | 0 |  |  | AVERAGE | 1209.04
| FURNACE – PV |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMSS96 0803BN; 80,000BTU; AFUE 96% | 2167.0795 | 2167.0795 | Furnace | 1278.34 | 1.05 | 1342.257 | 1.07 | 1436.215 | 1.3 | 1867.0795 | 1 | 300 | 2167.0795
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1537.9174 | 1537.9174 | Materials | 1105.62 | 1 | 1105.62 | 1.07 | 1183.0134 | 1.3 | 1537.9174 | 1 | 0 | 1537.9174
1 | PVC for Direct Venting | 328.6098 | 328.6098 | PVC | 236.24 | 1 | 236.24 | 1.07 | 252.7768 | 1.3 | 328.6098 | 1 | 0 | 328.6098
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1005.11 | [7 empty] | Total less LABOR | 5088.6246
|  80,000/76,800  |  | 7888.6246
|  |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
|  |  | 0 |  | 0803BN | 80000 | 1278.34 | 96% | PV | 1162.13
0
0
0
0
0
|  |  | 0 |  |  | AVERAGE | 1278.34
RHEEM / RUUD PV FURNACE
| FURNACE – PV |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | RHEEM/RUUD: M/N R96VA0402317MSA; 40,000BTU; AFUE 96% | 2892.301 | 2892.301 | Furnace | 1774.88 | 1.05 | 1863.624 | 1.07 | 1994.0777 | 1.3 | 2592.301 | 1 | 300 | 2892.301
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1537.9174 | 1537.9174 | Materials | 1105.62 | 1 | 1105.62 | 1.07 | 1183.0134 | 1.3 | 1537.9174 | 1 | 0 | 1537.9174
1 | PVC for Direct Venting | 328.6098 | 328.6098 | PVC | 236.24 | 1 | 236.24 | 1.07 | 252.7768 | 1.3 | 328.6098 | 1 | 0 | 328.6098
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1005.11 | [7 empty] | Total less LABOR | 5813.8461
|  40,000/38,400  |  | 8613.8461
|  |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
|  |  | 0 |  | 0402317MSA | 40000 | 1774.88 | 96% | PV | 1613.53
0
0
0
0
0
|  |  | 0 |  |  | AVERAGE | 1774.88
| FURNACE – PV |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | RHEEM/RUUD: M/N R96VA0602317MSA; 60,000BTU; AFUE 96% | 2767.6723 | 2767.6723 | Furnace | 1689.55 | 1.05 | 1774.0275 | 1.07 | 1898.2094 | 1.3 | 2467.6723 | 1 | 300 | 2767.6723
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1537.9174 | 1537.9174 | Materials | 1105.62 | 1 | 1105.62 | 1.07 | 1183.0134 | 1.3 | 1537.9174 | 1 | 0 | 1537.9174
1 | PVC for Direct Venting | 328.6098 | 328.6098 | PVC | 236.24 | 1 | 236.24 | 1.07 | 252.7768 | 1.3 | 328.6098 | 1 | 0 | 328.6098
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1005.11 | [7 empty] | Total less LABOR | 5689.2174
|  60,000/57,600  |  | 8489.2174
|  |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
|  |  | 0 |  | 0602317MSA | 60000 | 1689.55 | 96% | PV | 1689.55
0
0
0
0
0
|  |  | 0 |  |  | AVERAGE | 1689.55
GOODMAN PV FURNACE
| FURNACE – DV |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMSS96 1005CNA; 96,000BTU; AFUE 96% | 2543.0251 | 2543.0251 | Furnace | 1535.74 | 1.05 | 1612.527 | 1.07 | 1725.4039 | 1.3 | 2243.0251 | 1 | 300 | 2543.0251
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1537.9174 | 1537.9174 | Materials | 1105.62 | 1 | 1105.62 | 1.07 | 1183.0134 | 1.3 | 1537.9174 | 1 | 0 | 1537.9174
1 | PVC for Direct Venting | 328.6098 | 328.6098 | PVC | 236.24 | 1 | 236.24 | 1.07 | 252.7768 | 1.3 | 328.6098 | 1 | 0 | 328.6098
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1005.11 | [7 empty] | Total less LABOR | 5464.5702
|  100,000/96,000  |  | 8264.5702
|  |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
|  |  | 0 |  | 1005CNA | 100000 | 1535.74 | 96% | PV | 1396.13
0
0
0
0
0
|  |  | 0 |  |  | AVERAGE | 1535.74
| FURNACE – DV |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMSS96 1205DNA; 120,000BTU; AFUE 96% | 2727.3903 | 2727.3903 | Furnace | 1661.97 | 1.05 | 1745.0685 | 1.07 | 1867.2233 | 1.3 | 2427.3903 | 1 | 300 | 2727.3903
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1537.9174 | 1537.9174 | Materials | 1105.62 | 1 | 1105.62 | 1.07 | 1183.0134 | 1.3 | 1537.9174 | 1 | 0 | 1537.9174
1 | PVC for Direct Venting | 328.6098 | 328.6098 | PVC | 236.24 | 1 | 236.24 | 1.07 | 252.7768 | 1.3 | 328.6098 | 1 | 0 | 328.6098
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1005.11 | [7 empty] | Total less LABOR | 5648.9354
|  120,000/115,200  |  | 8448.9354
|  |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
|  |  | 0 |  | 1205DNA | 120000 | 1661.97 | 96% | PV | 1510.88
0
0
0
0
0
|  |  | 0 |  |  | AVERAGE | 1661.97
Regular Description – with tune and clean
NO A/C | After a tune and clean, and adjusting the gas control valve, still have flame roll out. Will need a new DHW. Must: shut off gas; disconnect gas line; disconnect distribution duct work; remove old transition piece connecting to distribution duct work; remove old system; patch flue pipe hole in chimney; install new system; install/adjust transition section to fit to distribution duct work and connect to new furnace; drill for installing PVC to the outside; install PVC piping; connect to gas pipe; make electrical connections; turn on gas and check for leaks; commission system; set for normal operation.
Twin system description
TWIN SYSTEMS | Existing system is an oil-to-gas conversion and is not repairable and must be replaced. To maximize the heating potential, the proposal is to replace the existing 189,000BTU system at 79% AFUE with two 92,150BTU systems both at 95% AFUE. Must: shut off gas; break gas line connection; break connection to distribution duct work; remove old transition piece connecting to distribution duct work; remove old system; remove connection to the chimney and seal the hole; install new systems; install/adjust transition sections to fit to distribution duct work and make connection; as these are direct vent systems, must install PVC direct vent connections from both furnaces to the outside, which will require core drilling through the basement wall for proper placement of the PVC; must upgrade 35 feet of gas delivery line from 3/4” to 1-1/4” to meet the PSI requirements of the twin systems; make gas pipe connections; make electrical connections; turn on gas and check for leaks; commission both systems; set systems for normal operation.
FORCED HOT AIR – 80% ATMOSPHERIC | FORCED HOT AIR – 80% ATMOSPHERIC |  | #VALUE!
Quantity | Description | UNIT PRICE | LINE TOTAL
| FURNACE |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMS8040; 40,000BTU; AFUE 80% | 1291.5048 | 1291.5048 | Furnace | 712.8 | 1 | 712.8 | 1.07 | 762.696 | 1.3 | 991.5048 | 1 | 300 | 1291.5048
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1661.8833 | 1661.8833 | Materials | 1194.74 | 1 | 1194.74 | 1.07 | 1278.3718 | 1.3 | 1661.8833 | 1 | 0 | 1661.8833
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1086.13 | [7 empty] | Total less LABOR | 4008.406
|  40,000/38,400  |  | 6808.406
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
1 | Material | 148.61 | 148.61 |  | 0403 | 40000 | 712.8 | 80% | Normal | 648
1 | Labor | 175 | 175
323.61
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● | 2010 | 2010
1 | Permit Chimney Liner | 125 | 125
| 0 |  | 2135 |  |  | AVERAGE | 712.8
| FURNACE |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMS8060; 60,000BTU; AFUE 80% | 1389.6259 | 1389.6259 | Furnace | 783.34 | 1 | 783.34 | 1.07 | 838.1738 | 1.3 | 1089.6259 | 1 | 300 | 1389.6259
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1661.8833 | 1661.8833 | Materials | 1194.74 | 1 | 1194.74 | 1.07 | 1278.3718 | 1.3 | 1661.8833 | 1 | 0 | 1661.8833
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1086.13 | [7 empty] | Total less LABOR | 4106.5272
|  60,000/57,600  |  | 6906.5272
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
1 | Material | 148.61 | 148.61 |  | 0603 | 60000 | 783.34 | 80% | Normal | 712.13
1 | Labor | 175 | 175
323.61
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● | 2010 | 2010
1 | Permit Chimney Liner | 125 | 125
| 0 |  | 2135 |  |  | AVERAGE | 783.34
| FURNACE |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMS8080; 80,000BTU; AFUE 80% | 1475.701 | 1475.701 | Furnace | 845.22 | 1 | 845.22 | 1.07 | 904.3854 | 1.3 | 1175.701 | 1 | 300 | 1475.701
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1661.8833 | 1661.8833 | Materials | 1194.74 | 1 | 1194.74 | 1.07 | 1278.3718 | 1.3 | 1661.8833 | 1 | 0 | 1661.8833
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1086.13 | [7 empty] | Total less LABOR | 4192.6022
|  40,000/38,400  60,000/57,600  80,000/76,800  |  | 6992.6022
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
1 | Material | 148.61 | 148.61 |  | 080 | 80000 | 845.22 | 80% | Normal | 768.38
1 | Labor | 175 | 175
323.61
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● | 2010 | 2010
1 | Permit Chimney Liner | 125 | 125
| 0 |  | 2135 |  |  | AVERAGE | 845.22
| FURNACE |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMS8100; 100,000BTU; AFUE 80% | 1609.9603 | 1609.9603 | Furnace | 941.74 | 1 | 941.74 | 1.07 | 1007.6618 | 1.3 | 1309.9603 | 1 | 300 | 1609.9603
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1661.8833 | 1661.8833 | Materials | 1194.74 | 1 | 1194.74 | 1.07 | 1278.3718 | 1.3 | 1661.8833 | 1 | 0 | 1661.8833
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1086.13 | [7 empty] | Total less LABOR | 4326.8616
|  100,000/96,000  120,000/115,200  |  | 7126.8616
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
1 | Material | 148.61 | 148.61 |  | 1005CN | 100000 | 941.74 | 80% | Normal | 856.13
1 | Labor | 175 | 175
323.61
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● | 2010 | 2010
1 | Permit Chimney Liner | 125 | 125
| 0 |  | 2135 |  |  | AVERAGE | 941.74
| FURNACE |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Goodman: M/N GMS8120; 120,000BTU; AFUE 80% | 1807.9135 | 1807.9135 | Furnace | 1084.05 | 1 | 1084.05 | 1.07 | 1159.9335 | 1.3 | 1507.9135 | 1 | 300 | 1807.9135
1 | Materials – gas pipe & fittings; transition piece and other fittings | 1661.8833 | 1661.8833 | Materials | 1194.74 | 1 | 1194.74 | 1.07 | 1278.3718 | 1.3 | 1661.8833 | 1 | 0 | 1661.8833
1 | Electrical hook up | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Delivery and Haul Away | 270.007 | 270.007 | Dlvry & Haul | 194.11 | 1 | 194.11 | 1.07 | 207.6977 | 1.3 | 270.007 | 1 | 0 | 270.007
1 | Permit EO $730 | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
16 | Labor for two men at 8 hours each man | 175 | 2800 | Materials | 1086.13 | [7 empty] | Total less LABOR | 4524.8148
|  100,000/96,000  120,000/115,200  |  | 7324.8148
| UPGRADE DHW FLUE 4” – CHECK LENGTH OF RUN for $$ and LABOR |  | 0 |  | GOODMAN | BTU IN | COST | AFUE | Flue Min.
1 | Material | 148.61 | 148.61 |  | 1205 | 120000 | 1084.05 | 80% | Normal | 985.5
1 | Labor | 175 | 175
323.61
CHIMNEY LINER and CAP
1 | Liner ● IRV, TOT, S-ORNG, W-ORNG ● ADD $600 for clack-out ● | 2010 | 2010
1 | Permit Chimney Liner | 125 | 125
| 0 |  | 2135 |  |  | AVERAGE | 1084.05
DHW Tune and Clean – Also basic description
NO A/C | After a tune and clean, and adjusting the gas control valve, still have flame roll out. Will need a new furnace. Must: shut off gas; disconnect gas line; disconnect distribution duct work; remove old transition piece connecting to distribution duct work; remove old system; install new system; install/adjust transition section to fit to distribution duct work and connect to new furnace; connect to gas pipe; make electrical connections; turn on gas and check for leaks; commission system; set for normal operation.
END

## GCV
GAS CONTROL VALVE
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| GAS CONTROL VALVE |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Material | 165 | 215 | 375.418 | 375.418 | Material | 198 | 1 | 198 | 1.07 | 211.86 | 1.3 | 275.418 | 1 | 100 | 375.418
3 | Labor |  |  | 175 | 525 |  |  |  | 0 |  | 0 |  | 0 |  | 0 | 0
[5 empty] | 900.418 |  |  |  | 0 |  | 0 |  | 0 |  | 0 | 0
[9 empty] | 0 |  | 0 |  | 0 |  | 0 | 0
[9 empty] | 0 |  | 0 |  | 0 |  | 0 | 0
[6 empty] | Material | 180 | [7 empty] | Total less LABOR | 375.418
Description
Must: shut off gas; disconnect house gas line; disconnect gas line connection to heating system; remove low voltage wiring; remove gas control valve; install replacement gas control valve; connect low voltage wiring; connect gas house line; connect gas line to heating system; turn on gas; check for leaks; re-commision heating system; set for normal operation.
END

## COMBO UNITS
COMBO UNITS – 95%
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| COMBO UNIT |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White: M/N BMFTCW199NA1XN; 199,000 BTU; AFUE 95% |  |  | 4814.05 | 4814.05 | Boiler | 4514.05 | 1 | 4514.05 | 1 | 4514.05 | 1 | 4514.05 | 1 | 300 | 4814.05
1 | Materials |  |  | 2183.26 | 2183.26 | Materials | 2183.26 | 1 | 2183.26 | 1 | 2183.26 | 1 | 2183.26 | 1 | 0 | 2183.26
1 | PVC Concentric vent with termination kit and piping |  |  | 361.47 | 361.47 | PVC Kit | 361.47 | 1 | 361.47 | 1 | 361.47 | 1 | 361.47 | 1 | 0 | 361.47
1 | Electrical hook up |  |  | 300.01 | 300.01 | Elec Hook Up | 300.01 | 1 | 300.01 | 1 | 300.01 | 1 | 300.01 | 1 | 0 | 300.01
1 | Delivery and Haul Away |  |  | 394.35 | 394.35 | Dlvry & Haul | 394.35 | 1 | 394.35 | 1 | 394.35 | 1 | 394.35 | 1 | 0 | 394.35
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
24 | Labor for two men at 12 hours each man |  |  | 175 | 4200 | Materials | 1984.78 | [7 empty] | Total less LABOR | 8538.14
[5 empty] | 12738.14 | PVC Kit | 328.61
EXPANSION TANK
1 | Expansion Tank |  |  | 86.2698 | 86.2698 |  | BW | BTU IN | COST | AFUE | Flue Min.
1 | Tee and Ball Valve |  |  | 35.0532 | 35.0532 |  | BMFTCW199 | 199000 | 4514.05 | 95% | PVC Kit – above | 4103.68
1 | Labor |  |  | 175 | 175
296.323
BACK FLOW PREVENTER
1 | Back Flow Preventer |  |  | 230.065 | 230.065
1 | Labor |  |  | 175 | 175
[5 empty] | 405.065 |  |  | AVERAGE | 4514.05 | (UNIT COST for Boiler above)
NEUTRALIZER CONDENSATE PUMP
1 | Pump |  |  | 247.5 | 247.5
2 | Labor |  |  | 175 | 350
597.5
Combo Description
Must: shut off gas; shut off water; disconnect water line connection; disconnect gas line connection; drain down boiler; disconnect from house line; remove old boiler; install replacement boiler; connect to house line; connect to water line; fill boiler; test for water leaks; connect to gas line; test for gas leaks; commission boiler and bleed house lines; set for normal operation.
END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END

## Tankless DHW
TANKLESS DHW
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| TANKLESS WATER HEATER – WALL MOUNT |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Bradford White: RTG-K-199-N1 |  |  | 1950.125 | 1950.125 | Boiler | 1346.25 | 1 | 1346.25 | 1 | 1346.25 | 1.3 | 1750.125 | 1 | 200 | 1950.125
1 | Materials |  |  | 250.38 | 250.38 | Materials | 180 | 1 | 180 | 1.07 | 192.6 | 1.3 | 250.38 | 1 | 0 | 250.38
1 | Electrical hook up |  |  | 300.0109 | 300.0109 | Elec Hook Up | 215.68 | 1 | 215.68 | 1.07 | 230.7776 | 1.3 | 300.0109 | 1 | 0 | 300.0109
1 | Permit EO $730 |  |  | 485 | 485 | Permit | 485 | 1 | 485 | 1 | 485 | 1 | 485 | 1 | 0 | 485
6 | Labor for two men 3 hours each |  |  | 175 | 1050 | [9 empty] | Total less LABOR | 2985.5159
4035.5159
[7 empty] | BW | BTU IN | COST | AFUE | Flue Min.
[7 empty] | RTG-K-199-N1 | 199MBTU | 1346.25 |  | 2” 120’ ¦¦ 3” 560’
[8 empty] | AVERAGE | 1346.25
Combo Description
To do this we must: shut off water; disconnect water lines; drain DHW; shut off gas; disconnect gas line; disconnect flue pipe; remove existing DHW; install new DHW; connect to water lines; fill DHW; test for water leaks; connect flue pipe; connect to gas line; turn on gas; test for gas leaks; commission DHW; set for normal operation.
END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END | END

## Neutralizer Condensate Pump
NEUTRALIZER CONDENSATE Pump
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| NEUTRALIZER CONDENSATE PUMP |  |  |  | 0 | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Pump | 165 | 215 | 247.5 | 247.5 | Pump | 247.5 | 1 | 247.5 | 1 | 247.5 | 1 | 247.5 | 1 | 0 | 247.5
2 | Labor |  |  | 175 | 350 | Pump | 225 | [7 empty] | Total less LABOR | 247.5
597.5
Description
The aquastat on the boiler has failed and must be replaced. To do this, must: shut off the boiler; drain down the boiler; remove the expansion tank; remove the failing aquastat; install the replacement aquastat; re-install the expansion tank; re-fill the boiler; bleed the system; set for normal operation.
END

## T-STATs
LINE VOLT THERMOSTAT
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| Line Volt Thermostat | 165 | 215
1 | Materials |  |  | 276 | 276
1 | Labor |  |  | 175 | 175
451
Description
Installed line volt t-stat
DIGITAL THERMOSTAT
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
T-STAT
1 | Materials |  |  | 181 | 181 | 181 | Based on CONTRACT pricing
1 | Labor |  |  | 175 | 175
356
Description
Installed t-stat
END

## Sump Pump
SUMP PUMP
Quantity | Description |  |  | UNIT PRICE | LINE TOTAL
| SUMP PUMP |  |  |  |  | DESCRIPTION | UNIT COST | Increase % | Cost + Increase | Tax | Tax + Cost | Mark Up | TOTAL | QTY | WRNTY | Total Cost
1 | Material | 165 | 215 | 403.3613 | 403.3613 | sump pump | 156 | 1.1 | 171.6 | 1.07 | 183.612 | 1.3 | 238.6956 | 1 | 50 | 288.6956
3 | Labor |  |  | 175 | 525 | PVC pipe 10' | 6.6 | 1.1 | 7.26 | 1.07 | 7.7682 | 1.3 | 10.0987 | 4 | 0 | 40.3946
[5 empty] | 928.3613 | PVC elbows | 1 | 1.1 | 1.1 | 1.07 | 1.177 | 1.3 | 1.5301 | 1 | 0 | 1.5301
[5 empty] | 0 | PVC couplings | 0.83 | 1.1 | 0.913 | 1.07 | 0.97691 | 1.3 | 1.27 | 4 | 0 | 5.0799
[5 empty] | 0 | check valve | 29.42 | 1.1 | 32.362 | 1.07 | 34.6273 | 1.3 | 45.0155 | 1 | 0 | 45.0155
[5 empty] | 0 | Hangars | 1.48 | 1.1 | 1.628 | 1.07 | 1.742 | 1.3 | 2.2645 | 10 | 0 | 22.6455
[8 empty] | Increase % | [6 empty] | Total less LABOR | 403.3613
1
Description
The sump pump failed. Propose to: install a new sump pump; install a check valve so the discharge water does not come back into the sump pit; install PVC for a discharge line from the sump pump to the outside of the house; must core drill through the foundation to properly route the PVC outside the house. Once completed, fill sump pit with water and test the pump; check for water leaks; set for normal operation.
Open pit
Open sump pit in basement. Original sump pump failed. Propose to install new sump pump. Propose to: install a new sump pump; install a check valve so the discharge water does not come back into the sump pit; install PVC for a discharge line from the sump pump to the outside of the house; must core drill through the foundation to properly route the PVC outside the house. Will also need to dig sump pit deeper to fit new pump and gravel base. Once completed, fill sump pit with water and test the pump; check for water leaks; set for normal operation.
END