## Pressure_design
Main information				Cost

H = 15 m	30	m		Unit pipe cost	3,50 €	€/mm*D/m
L = 100 m	100	m		Penalty	0,06 €	€/kWst
P = 13 bara	13	bara		Running hours	8000	h/yr
Vinlet = 11,8 kg/s	1,78328547680218	m3/s		Maintenance	2 %	Of installation cost
k	0,1	mm		Discount rate	10,00 %
Dynamic viscosity	0,0001408	Pa*S		Present value	20	year
Kinemic viscosity	1,61E-07	m2/s
Density (kg/m3)	6,617
Gravity	9,81
Power out	5,50E+03	kW
Power penalty	200	kW/bar

				PIPE	Pressure		Cost
Re number	f	A	V	Diameter	Drop	Drop2	Pipe installation	Maintenance	Power penalty	Penalty and maintenance	Total Cost
7,05E+07	0,0167067688592829	0,0314159265358979	56,7637397154109	200	13,7184632868501	0,00890503	700,00 €	14,00 €	854,88 €	7.397,29 €	8.097,29 €
5,64E+07	0,0159067118313629	0,0490873852123405	36,328793417863	250	4,27999586648402	0,00277826	875,00 €	17,50 €	266,71 €	2.419,67 €	3.294,67 €
4,70E+07	0,0152973204566657	0,0706858347057704	25,2283287624048	300	1,65413926413235	0,00107375	1.050,00 €	21,00 €	103,08 €	1.056,36 €	2.106,36 €
4,03E+07	0,0148112666436802	0,0962112750161874	18,5350986825831	350	0,74099445537817	0,00048100	1.225,00 €	24,50 €	46,18 €	601,70 €	1.826,70 €	Optimal D
3,52E+07	0,0144108658239807	0,125663706143592	14,1909349288527	400	0,36978824160124	0,00024004	1.400,00 €	28,00 €	23,04 €	434,56 €	1.834,56 €
3,13E+07	0,0140730681850526	0,159043128087983	11,2125905610688	450	0,200396071049258	0,00013008	1.575,00 €	31,50 €	12,49 €	374,49 €	1.949,49 €

Design pressure	1,4	X operating pressure
Design temperature		Saturated vapor @ design pressure
Seamless pipe	1	z
Material		P235GH acc. to EN 10216
Temp	180	°C

f @ 175	178,5	MPa
F @ 187,5	174,25
F @ 181	176,375	MPa

Pc	16,25
D0	350
f	176,375
e	0,000992204110559887	m
	0,992204110559887	mm
This is without secondary Y axis.

Secondary Y axis is defined by me, but I would love to be able to reference Pressure drop 1

X axis shoudl show Diameter